## 意见跟踪表
技术协议及图纸认可意见跟踪表（导出 2026-11-06 00:20，共 189 条） | [5 empty] | 统计（自动）： | 意见总数 |  | 未关闭 |  | A类未关闭 |  | B类未关闭 |  | C类未关闭 |  | 回复超期 |  |  |  | 图例：红=回复超期/缺资料；黄=临期或未关闭；浅橙=迟复；灰底=公式
编号 | 协议编号 | 设备名称 | 厂家名称 | 技术协议认可阶段 | [8 empty] | TA 下发 |  | 定标计划 |  | 图纸认可阶段
|  |  |  | 意见提出方 | 提出时间 | 意见内容 | 意见类别 | 责任人 | 要求回复时间 | 实际回复时间 | 回复意见 | 关闭状态 | 计划下发时间 | 实际下发时间 | 计划时间 | 实际时间 | 认可资料 |  |  |  | 备注 | 认可函时间
[17 empty] | 外形图 | 总装图 | 管系接口资料 | 电气接口资料
TA-0001 | DEMO-TA-A014-01 | 救生筏 Life rafts | 厂家A | 船东 | 2026-07-19 | 救生筏及静水压力释放器须在船旗国主管机关和厂家认可的服务站检修 Please note that the inflatable liferafts should be serviced at servicing stations approved by the Flag State Administration and the manufacturer. Same applies to the Hydrostatic release units. | C |  |  | 2026-07-22 | 厂家A: Confirmed | 已关闭 | 2026-07-10 | 2026-07-10 | 2026-08-07 | 2026-08-10 | √ | √ | √ | √ | 中标厂家 | 2026-10-04
TA-0002 | DEMO-TA-A014-01 | 救生筏 Life rafts | 厂家A | 船东 | 2026-07-19 | 按船旗国要求，救生筏筒体加标船名、船籍港及登记号（对比色字体） In addition to the markings required under LSA Code 4.2.6.3, the name, port and number of the registry of the ship should be marked on the container of the inflatable liferaft. Each letter should be of a color contrasting with that of the container. These markings are required of all ships of this flag. | B |  |  | 2026-07-23 | 厂家A: Confirmed | 已关闭 | 2026-07-10 | 2026-07-10 | 2026-08-07 | 2026-08-10 | √ | √ | √ | √ | 中标厂家 | 2026-10-04
TA-0003 | DEMO-TA-A014-01 | 救生筏 Life rafts | 厂家A | 船东 | 2026-07-20 | 质保期须为交船后12个月，请确认 The warranty period shall be kept valid for twelve (12) months after the date of the Vessel Delivery. Please confirm | A |  |  | 2026-07-21 | 厂家A: Confirmed | 已关闭 | 2026-07-10 | 2026-07-10 | 2026-08-07 | 2026-08-10 | √ | √ | √ | √ | 中标厂家 | 2026-10-04
TA-0004 | DEMO-TA-A014-01 | 救生筏 Life rafts | 厂家A | 船东 | 2026-07-20 | 核实是否持有 ABS 船级社证书 Page 11: Verify if you hold ABS Class certificate | C |  |  | 2026-07-23 | 厂家A: MED certificate is issued by DNV, but ABS will accpet it | 已关闭 | 2026-07-10 | 2026-07-10 | 2026-08-07 | 2026-08-10 | √ | √ | √ | √ | 中标厂家 | 2026-10-04
TA-0005 | DEMO-TA-A014-02 | 救生筏 Life rafts | 厂家B | 船东 | 2026-11-03 | 明确静水压力释放器厂家及认证 Item 2: Hydrostatic releasing unit, maker and certification to be specified | C |  |  |  |  | 待回复 | 2026-10-08 | 2026-10-11 | 2026-11-10
TA-0006 | DEMO-TA-A014-02 | 救生筏 Life rafts | 厂家B | 船东 | 2026-10-28 | 提供不锈钢收放操作说明牌（正常及应急） Item 5: Instruction signs (stainless steel) to be provided for the operation procedure of launch and recovery (normal and emergency) | B |  |  |  |  | 待回复 | 2026-10-08 | 2026-10-11 | 2026-11-10
TA-0007 | DEMO-TA-A014-02 | 救生筏 Life rafts | 厂家B | 船东 | 2026-10-25 | 质保期须为交船后12个月，不接受到货后18个月 Item F: The warranty period shall be kept valid for twelve (12) months after the date of the Vessel Delivery. 18 months upon delivery of goods is not acceptable by the Owner. | A |  |  | 2026-10-28 | "We cannot accept just twelve (12) months after the date of the Vessel Delivery as this is an open clause and we don’t know when the vessel will be delivered, if the vessel delivery is postponed, such as postponed 3 years or even longer, we cannot afford the risk and extra cost. As a compromise, we propose ""The guarantee period shall be 12 months counting from the date on which the Buyer delivers the vessel to the Ship Owner, or 24 months after delivery of the contracted goods, whichever is earlier""" 【船东反馈】Noted. Aggre please revise | 已关闭 | 2026-10-08 | 2026-10-11 | 2026-11-10
TA-0008 | DEMO-TA-A014-02 | 救生筏 Life rafts | 厂家B | 船东 | 2026-10-26 | 救生筏及静水压力释放器须在船旗国主管机关和厂家认可的服务站检修 Please note that the inflatable liferafts should be serviced at servicing stations approved by the Flag State Administration and the manufacturer. Same applies to the Hydrostatic release units. | C |  |  | 2026-10-31 | Confirm | 已认可待落实 | 2026-10-08 | 2026-10-11 | 2026-11-10
TA-0009 | DEMO-TA-A014-02 | 救生筏 Life rafts | 厂家B | 船东 | 2026-10-26 | 按船旗国要求，救生筏筒体加标船名、船籍港及登记号（对比色字体） In addition to the markings required under LSA Code 4.2.6.3, the name, port and number of the registry of the ship should be marked on the container of the inflatable liferaft. Each letter should be of a color contrasting with that of the container. These markings are required of all ships of this flag. | B |  |  | 2026-10-31 | Confirm | 已回复待确认 | 2026-10-08 | 2026-10-11 | 2026-11-10
TA-0010 | DEMO-TA-A014-02 | 救生筏 Life rafts | 厂家B | 船东 | 2026-11-05 | 核实是否持有 ABS 船级社证书 Verify if you hold ABS Class certificate | C |  |  |  |  | 待回复 | 2026-10-08 | 2026-10-11 | 2026-11-10
TA-0011 | DEMO-TA-A014-02 | 救生筏 Life rafts | 厂家B | 船东 | 2026-10-30 | 救生筏架及释放臂材料未明确，应为镀锌，请确认 Page 17 / Liferaft Rack: Material of the liferaft rack and deployment arm is not specified. Should be galvanised, please confirm | B |  |  |  |  | 待回复 | 2026-10-08 | 2026-10-11 | 2026-11-10
TA-0012 | DEMO-TA-A015-01 | 救生筏吊架 Liferaft Davits | 厂家C | 船东 | 2026-06-16 | 船旗国为船旗国，TA 须体现并满足船旗国要求 Vessel's flag state is specified by the Owner. Please capture this at the TA and comply with the prerequisites of the flag state, where necessary. | B |  |  | 2026-06-21 | The details pertaining to the flag state have been duly specified on the front page of the Technical Agreement. | 已关闭 | 2026-06-09 | 2026-06-12 | 2026-07-11 | 2026-07-11 | √ | √ | √ | √ | 中标厂家 | 2026-08-22
TA-0013 | DEMO-TA-A015-01 | 救生筏吊架 Liferaft Davits | 厂家C | 船东 | 2026-06-16 | 核实是否持有 ABS 船级社证书 Please verify if you hold ABS Class certificate | C |  |  | 2026-06-18 | only MED certificate can be provided. | 已关闭 | 2026-06-09 | 2026-06-12 | 2026-07-11 | 2026-07-11 | √ | √ | √ | √ | 中标厂家 | 2026-08-22
TA-0014 | DEMO-TA-A015-01 | 救生筏吊架 Liferaft Davits | 厂家C | 船东 | 2026-06-16 | 涂装仅含底漆，须明确完整涂层体系（各道涂层及类型） Page 12 / 2: Please clarify why the coating system includes primer only. Compete paint system (all coats and types) to be specified | B |  |  | 2026-06-19 | Will be provided for delivery of the topcoat. | 已关闭 | 2026-06-09 | 2026-06-12 | 2026-07-11 | 2026-07-11 | √ | √ | √ | √ | 中标厂家 | 2026-08-22
TA-0015 | DEMO-TA-A015-02 | 救生筏吊架 Liferaft Davits | 厂家D | 船东 | 2026-06-13 | TA 须明确质保期起算日期 TA to specify the warranty starting date | A |  |  | 2026-06-16 | The warranty period shall commence on the date of the vessel’s delivery and remain valid for a period of twelve (12) months. | 已关闭 | 2026-05-31 | 2026-06-04 | 2026-06-30 | 2026-06-29 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0016 | DEMO-TA-A015-02 | 救生筏吊架 Liferaft Davits | 厂家D | 船东 | 2026-06-13 | 船旗国为船旗国（目前为中文），TA 须体现并满足船旗国要求 Vessel's flag state is specified by the Owner (currently in Chinese). Please capture this at the TA and comply with the prerequisites of the flag state, where necessary. | B |  |  | 2026-06-16 | The details pertaining to the flag state have been duly specified on the front page of the Technical Agreement. | 已关闭 | 2026-05-31 | 2026-06-04 | 2026-06-30 | 2026-06-29 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0017 | DEMO-TA-A015-02 | 救生筏吊架 Liferaft Davits | 厂家D | 船东 | 2026-06-14 | 核实是否持有 ABS 船级社证书 Please verify if you hold ABS Class certificate | C |  |  | 2026-06-15 | The American Bureau of Shipping (ABS) acknowledges the validity of the European Union Marine Equipment Directive (MED) Certificate for statutory compliance purposes, whereas such certification does not constitute an ABS-classed product approval. | 已关闭 | 2026-05-31 | 2026-06-04 | 2026-06-30 | 2026-06-29 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0018 | DEMO-TA-C001-01 | 涂料 Paint | 厂家E | 船东 | 2026-06-16 | 防污漆方案是否考虑了船舶营运工况 Kindly advise if the vessel's operational profile is considered for the antifouling paint scheme. | A |  |  | 2026-06-17 | The paint system (including the antifouling paint) has been formulated in strict accordance with the requirements of your specification. 【船东反馈】Not clear reply. Please Review 【第2轮回复】At present, the service speed I know is 11.5 knots, and the highest seawater temperature is 32 degrees Celsius and the lowest is 0 degrees Celsius. We need to know the average seawater temperature. In addition, we also need to know the operating rate of your vessel in order to provide the supplier with more suitable matching. | 已关闭 | 2026-06-08 | 2026-06-09 | 2026-07-06 | 2026-07-04 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0019 | DEMO-TA-C001-01 | 涂料 Paint | 厂家E | 船东 | 2026-06-16 | 说明防污漆自抛光所需的最低航速 Please advise the minimum vessel speed for the antifouling paint to self-polish itshelf | A |  |  | 2026-06-18 | The minimum ship speed required by 厂家F is above 6 knots, 厂家H requires above 10 knots, 厂家G requires above 3 knots, and 厂家E requires above 9 knots. Please be informed. 【船东反馈】According to the reply and the vessel's type, all Antifouling paints from the makers, does not meet requirments. Due to very low speeds the AF paint should be capable for long lay off periods. | 已关闭 | 2026-06-08 | 2026-06-09 | 2026-07-06 | 2026-07-04 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0020 | DEMO-TA-C001-02 | 涂料 Paint | 厂家F | 船东 | 2026-10-26 | 防污漆方案是否考虑了船舶营运工况 Kindly advise if the vessel's operational profile is considered for the antifouling paint scheme. | A |  |  | 2026-10-27 | The paint system (including the antifouling paint) has been formulated in strict accordance with the requirements of your specification. 【船东反馈】Not clear reply. Please Review 【第2轮回复】厂家E considers the matching of anti fouling paint based on a 50% operating rate and a speed of 9-10 knots. 厂家F suggests considering a minimum speed of 6 knots. 厂家G requires a minimum of 3 anti fouling paint matching requirements. The minimum requirement for 厂家H is 10 or more sections. | 已关闭 | 2026-10-03 | 2026-10-04 | 2026-11-21 |  | NA | NA | NA | NA | 中标厂家
TA-0021 | DEMO-TA-C001-02 | 涂料 Paint | 厂家F | 船东 | 2026-11-05 | 说明防污漆自抛光所需的最低航速 Please advise the minimum vessel speed for the antifouling paint to self-polish itshelf | A |  |  |  |  | 待回复 | 2026-10-03 | 2026-10-04 | 2026-11-21 |  | NA | NA | NA | NA | 中标厂家
TA-0022 | DEMO-TA-C001-03 | 涂料 Paint | 厂家G | 船东 | 2026-07-30 | 防污漆方案是否考虑了船舶营运工况 Kindly advise if the vessel's operational profile is considered for the antifouling paint scheme. | A |  |  | 2026-08-01 | The paint system (including the antifouling paint) has been formulated in strict accordance with the requirements of your specification. 【船东反馈】Not clear reply. Please Review 【第2轮回复】At present, the service speed I know is 11.5 knots, and the highest seawater temperature is 32 degrees Celsius and the lowest is 0 degrees Celsius. We need to know the average seawater temperature. In addition, we also need to know the operating rate of your vessel in order to provide the supplier with more suitable matching. | 已关闭 | 2026-07-16 | 2026-07-20 | 2026-08-14 | 2026-08-16 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0023 | DEMO-TA-C001-03 | 涂料 Paint | 厂家G | 船东 | 2026-07-27 | 说明防污漆自抛光所需的最低航速 Please advise the minimum vessel speed for the antifouling paint to self-polish itshelf | A |  |  | 2026-07-30 | The minimum ship speed required by 厂家F is above 6 knots, 厂家H requires above 10 knots, 厂家G requires above 3 knots, and 厂家E requires above 9 knots. Please be informed. 【船东反馈】According to the reply and the vessel's type, all Antifouling paints from the makers, does not meet requirments. Due to very low speeds the AF paint should be capable for long lay off periods. 【第2轮回复】At present, the service speed I know is 11.5 knots, and the highest sea temperature is 32 degrees Celsius and the lowest is 0 degrees Celsius. We need to know the average temperature of seawater. In addition, we also need to understand the operating rate of your vessel in order to provide suppliers with more suitable parameters for you to consider more suitable matching. | 已关闭 | 2026-07-16 | 2026-07-20 | 2026-08-14 | 2026-08-16 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0024 | DEMO-TA-C001-04 | 涂料 Paint | 厂家H | 船东 | 2026-07-12 | 防污漆方案是否考虑了船舶营运工况 Kindly advise if the vessel's operational profile is considered for the antifouling paint scheme. | A |  |  | 2026-07-15 | The paint system (including the antifouling paint) has been formulated in strict accordance with the requirements of your specification. 【船东反馈】Not clear reply. Please Review 【第2轮回复】At present, the service speed I know is 11.5 knots, and the highest sea temperature is 32 degrees Celsius and the lowest is 0 degrees Celsius. We need to know the average temperature of seawater. In addition, we also need to understand the operating rate of your vessel in order to provide suppliers with more suitable parameters for you to consider more suitable matching. | 已关闭 | 2026-07-03 | 2026-07-08 | 2026-08-14 | 2026-08-20 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0025 | DEMO-TA-C001-04 | 涂料 Paint | 厂家H | 船东 | 2026-07-14 | 说明防污漆自抛光所需的最低航速 Please advise the minimum vessel speed for the antifouling paint to self-polish itshelf | A |  |  | 2026-07-15 | The minimum ship speed required by 厂家F is above 6 knots, 厂家H requires above 10 knots, 厂家G requires above 3 knots, and 厂家E requires above 9 knots. Please be informed. 【船东反馈】According to the reply and the vessel's type, all Antifouling paints from the makers, does not meet requirments. Due to very low speeds the AF paint should be capable for long lay off periods. 【第2轮回复】I did not understand the actual operating parameters of the ship in the early stage. Please provide me with the minimum sailing speed, operating rate, and average seawater temperature. I will consider asking the supplier to reconsider the matching of anti fouling paint. | 已关闭 | 2026-07-03 | 2026-07-08 | 2026-08-14 | 2026-08-20 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0026 | DEMO-TA-E010-01 | 操纵台/主控制台 Manoeuvre Console / Main Console | 厂家I | 船东 | 2026-06-10 | 质保期需澄清 Warranty period to be clarified | A |  |  | 2026-06-12 | Warranty period will be determined in commercial contract. normally,One year after delivery or 24 months after delivery, whichever is due earlier | 已关闭 | 2026-05-25 | 2026-05-30 | 2026-07-03 | 2026-07-08 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0027 | DEMO-TA-E010-01 | 操纵台/主控制台 Manoeuvre Console / Main Console | 厂家I | 船东 | 2026-06-11 | 提供技术服务站（网点）位置 0-18: Please provide details of the technical service station location | C |  |  | 2026-06-13 | Please refer to the attached file. | 已关闭 | 2026-05-25 | 2026-05-30 | 2026-07-03 | 2026-07-08 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0028 | DEMO-TA-E010-01 | 操纵台/主控制台 Manoeuvre Console / Main Console | 厂家I | 船东 | 2026-06-10 | 明确各回路（1-2、2-2、3-2、4-2、5-2）断路器品牌 1-2, 2-2, 3-2, 4-2, 5-2: Please specify the maker of the breakers | C |  |  | 2026-06-11 | The breaker is of ABB brand. | 已关闭 | 2026-05-25 | 2026-05-30 | 2026-07-03 | 2026-07-08 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0029 | DEMO-TA-E010-01 | 操纵台/主控制台 Manoeuvre Console / Main Console | 厂家I | 船东 | 2026-06-08 | 主回路电缆颜色能否与本船标准一致 Please advise is it possible arrange cable color coding for main circuits same with vessel standard | B |  |  | 2026-06-15 | Yes, it's possible. | 已关闭 | 2026-05-25 | 2026-05-30 | 2026-07-03 | 2026-07-08 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0030 | DEMO-TA-E010-01 | 操纵台/主控制台 Manoeuvre Console / Main Console | 厂家I | 船东 | 2026-06-11 | 提供各控制台外形布置图 Please provide layout (outline view) dwg for each control console | B |  |  | 2026-06-16 | We'll provide them in approval drawing stage. | 已关闭 | 2026-05-25 | 2026-05-30 | 2026-07-03 | 2026-07-08 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0031 | DEMO-TA-E010-01 | 操纵台/主控制台 Manoeuvre Console / Main Console | 厂家I | 船东 | 2026-06-10 | 确认台内接线电缆截面 Please confirm Internal wiring cable size information | C |  |  | 2026-06-14 | Power circuit：Minimum 2.5mm2 Control circuit：Minimum 0.75mm2 | 已关闭 | 2026-05-25 | 2026-05-30 | 2026-07-03 | 2026-07-08 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0032 | DEMO-TA-E010-02 | 操纵台/主控制台 Manoeuvre Console / Main Console | 厂家J | 船东 | 2026-10-22 | 驾驶台控制台方案须满足 ABS NBLES 附加标志要求 For Wheelhouse control console, please confirm that the suggested solution will be according to ABS NBLES notation | A |  |  | 2026-10-25 | Agreed. Submit approval drawing of WCC to ABS for approval before manufacture | 已关闭 | 2026-09-26 | 2026-09-30 | 2026-11-22 |  | √ | 缺 | √ |  | 中标厂家
TA-0033 | DEMO-TA-E010-02 | 操纵台/主控制台 Manoeuvre Console / Main Console | 厂家J | 船东 | 2026-10-28 | 图纸仅使用英文 Drawings to be provided ONLY in English | C |  |  |  |  | 待回复 | 2026-09-26 | 2026-09-30 | 2026-11-22 |  | √ | 缺 | √ |  | 中标厂家
TA-0034 | DEMO-TA-E010-02 | 操纵台/主控制台 Manoeuvre Console / Main Console | 厂家J | 船东 | 2026-10-22 | 提供技术服务站（网点）位置 0-22: Please provide details of the technical service station location | C |  |  | 2026-10-24 | Please refer to the attached file. | 已关闭 | 2026-09-26 | 2026-09-30 | 2026-11-22 |  | √ | 缺 | √ |  | 中标厂家
TA-0035 | DEMO-TA-E010-02 | 操纵台/主控制台 Manoeuvre Console / Main Console | 厂家J | 船东 | 2026-10-23 | 明确控制台断路器品牌 Please confirm the maker of the brakers for console | C |  |  | 2026-10-25 | ABB or SIEMENS | 已关闭 | 2026-09-26 | 2026-09-30 | 2026-11-22 |  | √ | 缺 | √ |  | 中标厂家
TA-0036 | DEMO-TA-E010-02 | 操纵台/主控制台 Manoeuvre Console / Main Console | 厂家J | 船东 | 2026-10-27 | 铭牌能否采用白底黑字 Please confirm possibility install nameplates background white with black latters | B |  |  |  |  | 待回复 | 2026-09-26 | 2026-09-30 | 2026-11-22 |  | √ | 缺 | √ |  | 中标厂家
TA-0037 | DEMO-TA-E010-02 | 操纵台/主控制台 Manoeuvre Console / Main Console | 厂家J | 船东 | 2026-10-23 | 确认指示灯为 LED 型 Please confirm indication lamps LED type | C |  |  | 2026-10-24 | The indicator is LED type | 已认可待落实 | 2026-09-26 | 2026-09-30 | 2026-11-22 |  | √ | 缺 | √ |  | 中标厂家
TA-0038 | DEMO-TA-E010-02 | 操纵台/主控制台 Manoeuvre Console / Main Console | 厂家J | 船东 | 2026-10-24 | 提供各控制台外形布置图 Please provide layout (outline view) dwg for each control console | B |  |  | 2026-10-26 | We'll provide them in approval drawing stage. | 已认可待落实 | 2026-09-26 | 2026-09-30 | 2026-11-22 |  | √ | 缺 | √ |  | 中标厂家
TA-0039 | DEMO-TA-E010-02 | 操纵台/主控制台 Manoeuvre Console / Main Console | 厂家J | 船东 | 2026-10-24 | 确认台内接线电缆截面 Please confirm Internal wiring cable size information | C |  |  | 2026-10-29 | Power circuit：Minimum 2.5mm2 Control circuit：Minimum 1mm2 | 已关闭 | 2026-09-26 | 2026-09-30 | 2026-11-22 |  | √ | 缺 | √ |  | 中标厂家
TA-0040 | DEMO-TA-E010-03 | 操纵台/主控制台 Manoeuvre Console / Main Console | 厂家K | 船东 | 2026-07-11 | 提供台内外标签及标识标准 Please provide labels and marking standards inside and outside consoles | C |  |  | 2026-07-14 | Please refer to the attached file. | 已关闭 | 2026-07-03 | 2026-07-03 | 2026-08-07 | 2026-08-09 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0041 | DEMO-TA-E010-03 | 操纵台/主控制台 Manoeuvre Console / Main Console | 厂家K | 船东 | 2026-07-11 | 图纸仅使用英文 Drawings to be provided ONLY in English | C |  |  | 2026-07-15 | Drawings are in English only | 已关闭 | 2026-07-03 | 2026-07-03 | 2026-08-07 | 2026-08-09 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0042 | DEMO-TA-E010-04 | 操纵台/主控制台 Manoeuvre Console / Main Console | 厂家L | 船东 | 2026-07-25 | 驾驶台控制台方案须满足 ABS NBLES 附加标志要求 For Wheelhouse control console, please confirm that the suggested solution will be according to ABS NBLES notation | A |  |  | 2026-07-27 | Submit approval drawing of WCC to ABS for approval before manufacture | 已关闭 | 2026-07-13 | 2026-07-15 | 2026-08-13 | 2026-08-14 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0043 | DEMO-TA-E010-04 | 操纵台/主控制台 Manoeuvre Console / Main Console | 厂家L | 船东 | 2026-07-24 | 图纸仅使用英文 Drawings to be provided ONLY in English | C |  |  | 2026-07-25 | Agree | 已关闭 | 2026-07-13 | 2026-07-15 | 2026-08-13 | 2026-08-14 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0044 | DEMO-TA-E010-04 | 操纵台/主控制台 Manoeuvre Console / Main Console | 厂家L | 船东 | 2026-07-26 | 提供技术服务站（网点）位置 Please provide details of the technical service station location | C |  |  | 2026-07-31 | Submit approval drawing of WCC to ABS for approval before manufacture | 已关闭 | 2026-07-13 | 2026-07-15 | 2026-08-13 | 2026-08-14 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0045 | DEMO-TA-E010-04 | 操纵台/主控制台 Manoeuvre Console / Main Console | 厂家L | 船东 | 2026-07-24 | 明确控制台断路器品牌 Please confirm the maker of the brakers for console | C |  |  | 2026-07-29 | ABB or SIEMENS | 已关闭 | 2026-07-13 | 2026-07-15 | 2026-08-13 | 2026-08-14 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0046 | DEMO-TA-E010-04 | 操纵台/主控制台 Manoeuvre Console / Main Console | 厂家L | 船东 | 2026-07-25 | 质保期需澄清 Warranty period to be clarified | A |  |  | 2026-07-27 | The warranty period shall be kept valid for twelve (12) months after the date of the Vessel Delivery. | 已关闭 | 2026-07-13 | 2026-07-15 | 2026-08-13 | 2026-08-14 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0047 | DEMO-TA-E010-04 | 操纵台/主控制台 Manoeuvre Console / Main Console | 厂家L | 船东 | 2026-07-26 | 确认 UPS 电源（是否在供货范围内） Please confirm UPS power | A |  |  | 2026-07-28 | The console not include the UPS, which is provided by the third party | 已关闭 | 2026-07-13 | 2026-07-15 | 2026-08-13 | 2026-08-14 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0048 | DEMO-TA-E010-04 | 操纵台/主控制台 Manoeuvre Console / Main Console | 厂家L | 船东 | 2026-07-26 | 确认台内接线电缆截面 Please confirm Internal wiring cable size information | C |  |  | 2026-08-03 | Min. 0.75mm2 for control circuit, Min. 1.5mm2 for power circuit | 已关闭 | 2026-07-13 | 2026-07-15 | 2026-08-13 | 2026-08-14 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0049 | DEMO-TA-E010-04 | 操纵台/主控制台 Manoeuvre Console / Main Console | 厂家L | 船东 | 2026-07-25 | 提供各控制台外形布置图 Please provide layout (outline view) dwg for each control console | B |  |  | 2026-07-27 | We will provide approval drawing to yard after the business contract is awarded | 已关闭 | 2026-07-13 | 2026-07-15 | 2026-08-13 | 2026-08-14 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0050 | DEMO-TA-E018-01 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家I | 船东 | 2026-10-27 | 本船电制为 60Hz 而非 50Hz，须修改 0-4:Vessel is 60Hz and not 50Hz please amend | A |  |  | 2026-10-28 | Agree. We'll update it. | 已回复待确认 | 2026-09-28 | 2026-10-02 | 2026-11-14 |  | √ | 缺 | √ |  | 中标厂家
TA-0051 | DEMO-TA-E018-01 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家I | 船东 | 2026-10-27 | 所有配电板、分电箱、开关箱、母排等布置图（含仪表、设备、尺寸、标识、原理图）须送审 All switchboards, panels, switch boxes, bus bars etc. layouts with its respective instrumentation, equipment, dimensions, marking and diagrams etc to be be submitted for verification | B |  |  | 2026-11-01 | Agree. We'll submit it in approval drawing stage. | 已认可待落实 | 2026-09-28 | 2026-10-02 | 2026-11-14 |  | √ | 缺 | √ |  | 中标厂家
TA-0052 | DEMO-TA-E018-01 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家I | 船东 | 2026-10-27 | 直流电缆颜色：正极红、负极黑 0-6: DC cable: Positive:Red. Negative: Black. | B |  |  | 2026-11-01 | Agree. We'll update it. | 已关闭 | 2026-09-28 | 2026-10-02 | 2026-11-14 |  | √ | 缺 | √ |  | 中标厂家
TA-0053 | DEMO-TA-E018-01 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家I | 船东 | 2026-10-28 | 不接受记号/热印线号，须采用可打印热缩管或标签 0-9: Wire identification with hot marker is not acceptable. Printable shrinkable tube, or tags are accepted. | B |  |  | 2026-10-30 | Agree. We'll update it. | 已认可待落实 | 2026-09-28 | 2026-10-02 | 2026-11-14 |  | √ | 缺 | √ |  | 中标厂家
TA-0054 | DEMO-TA-E018-01 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家I | 船东 | 2026-10-28 | 所有配电板/箱外壳颜色须为 RAL 9001（奶白色） All switcboard/panels etc external colour to be equivalent to RAL 9001 (cream) | B |  |  | 2026-10-29 | Agree. We'll update it. | 已回复待确认 | 2026-09-28 | 2026-10-02 | 2026-11-14 |  | √ | 缺 | √ |  | 中标厂家
TA-0055 | DEMO-TA-E018-01 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家I | 船东 | 2026-10-28 | 应急/停泊发电机：确认主配电板恢复供电后应急发电机自动停机 Emergency/Harbor Generator: Kindly confirm that the em/cy gen will stop automaticaly once power from the main swbd will be restored. | B |  |  | 2026-11-01 | Confirm. | 已关闭 | 2026-09-28 | 2026-10-02 | 2026-11-14 |  | √ | 缺 | √ |  | 中标厂家
TA-0056 | DEMO-TA-E018-01 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家I | 船东 | 2026-10-29 | 应急/停泊发电机：说明停泊模式操作程序，澄清短时并车持续时长 Emergency/Harbor Generator: Kindly advise operation sequence on harbor mode.Kindly clarify the short-time synchronous parallel mode. How many seconds will this last? | B |  |  | 2026-11-04 | operation sequence on harbor mode： 1.Put the EG Operating Mode switch in harbor position； 2.Press the start button for the harbor generator； 3.Put the Synchroscope Switch in EG position； 4.Adjust the speed of the harbor generator to make its frequency slightly higher than the busbar； 5.Observe the Synchroscope and press the harbor generator closing button when the LED light rotates to 12 o'clock; 6.Adjust the speed of the harbor generator to transfer the load to the harbor generator, and then press the remote control open button of the transformer circuit breaker on the 440V ASB. Short-time synchronous parallel mode will last about 60 seconds. | 已关闭 | 2026-09-28 | 2026-10-02 | 2026-11-14 |  | √ | 缺 | √ |  | 中标厂家
TA-0057 | DEMO-TA-E018-01 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家I | 船东 | 2026-10-29 | 提供各配电板断路器、继电器、接触器、仪表、保护元件等品牌 Kindly provide maker of: Breaker/relays/ contactors/instuments/safety etc for all switchboards | C |  |  | 2026-10-31 | Breaker , Contactor to be ABB brand, relay to be of Weidmuller brand and instrument to be of Wuhan Xiangyi brand. | 已关闭 | 2026-09-28 | 2026-10-02 | 2026-11-14 |  | √ | 缺 | √ |  | 中标厂家
TA-0058 | DEMO-TA-E018-01 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家I | 船东 | 2026-10-29 | 提供主要配电板示意图/草图 Kindly provide indicative drawing/sketch from all the major switchboards. | B |  |  | 2026-11-03 | We'll provide them in approval drawing stage. | 已认可待落实 | 2026-09-28 | 2026-10-02 | 2026-11-14 |  | √ | 缺 | √ |  | 中标厂家
TA-0059 | DEMO-TA-E018-01 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家I | 船东 | 2026-10-29 | 提供以往项目参考照片 Please provide Indicative photos from past projects | C |  |  |  |  | 待回复 | 2026-09-28 | 2026-10-02 | 2026-11-14 |  | √ | 缺 | √ |  | 中标厂家
TA-0060 | DEMO-TA-E018-01 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家I | 船东 | 2026-10-30 | 确认试验板 24VDC 电源 9-3.: Please confirm 24 VDC supply for test panel | C |  |  | 2026-11-01 | Confirm. The DC24V comes from the inner DC power module. | 已关闭 | 2026-09-28 | 2026-10-02 | 2026-11-14 |  | √ | 缺 | √ |  | 中标厂家
TA-0061 | DEMO-TA-E018-01 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家I | 船东 | 2026-10-30 | 确认试验板按规格书提供 0–24VDC 及 0–440VAC 可调电源 9-5.: Please confirm for test panel 0-24 VDC and 0-440 VAC variable voltage supply according specification | B |  |  | 2026-11-04 | Agree. We'll update it. | 已回复待确认 | 2026-09-28 | 2026-10-02 | 2026-11-14 |  | √ | 缺 | √ |  | 中标厂家
TA-0062 | DEMO-TA-E018-01 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家I | 船东 | 2026-10-31 | 提供电缆截面清单（内部及外部接线） please provide list for cable size (internal and external wiring) | C |  |  | 2026-11-04 | Internal:Power circuit：Minimum 2.5mm2,Control circuit：Minimum 0.75mm2 external:The approved drawing stage will estimate the required cable size and length according to the detailed design. | 已关闭 | 2026-09-28 | 2026-10-02 | 2026-11-14 |  | √ | 缺 | √ |  | 中标厂家
TA-0063 | DEMO-TA-E018-02 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家J | 船东 | 2026-06-18 | 所有配电板、分电箱、开关箱、母排等布置图（含仪表、设备、尺寸、标识、原理图）须送审 All switchboards, panels, switch boxes, bus bars etc. layouts with its respective instrumentation, equipment, dimensions, marking and diagrams etc to be be submitted for verification | B |  |  | 2026-06-22 | Agree. We'll submit it in approval drawing stage. | 已关闭 | 2026-06-05 | 2026-06-07 | 2026-07-13 | 2026-07-16 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0064 | DEMO-TA-E018-02 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家J | 船东 | 2026-06-18 | 不接受记号/热印线号，须采用可打印热缩管或标签 0-9: Wire identification with marker is not acceptable. Printable shrinkable tube, or tags are accepted. | B |  |  | 2026-06-21 | Cable numbers are printed using heat shrink tubes | 已关闭 | 2026-06-05 | 2026-06-07 | 2026-07-13 | 2026-07-16 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0065 | DEMO-TA-E018-02 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家J | 船东 | 2026-06-18 | 图纸仅使用英文 0-12: Language of the drawings to be only in English | C |  |  | 2026-06-23 | Agree | 已关闭 | 2026-06-05 | 2026-06-07 | 2026-07-13 | 2026-07-16 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0066 | DEMO-TA-E018-02 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家J | 船东 | 2026-06-17 | 接触器、热继电器须与断路器同品牌（ABB/西门子），不接受国产品牌 0-23: The contactor,thermal overload relay to be same as the Breakers(ABB/Siemens) for uniformity.No Chinese maker is accepted. | A |  |  | 2026-06-19 | Agreed. The breaker to be of ABB or siemens brand | 已关闭 | 2026-06-05 | 2026-06-07 | 2026-07-13 | 2026-07-16 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0067 | DEMO-TA-E018-02 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家J | 船东 | 2026-06-18 | 所有配电板/箱外壳颜色须为 RAL 9001（奶白色） All switcboard/panels etc external colour to be equivalent to RAL 9001 (cream) | B |  |  | 2026-06-20 | Agreed. | 已关闭 | 2026-06-05 | 2026-06-07 | 2026-07-13 | 2026-07-16 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0068 | DEMO-TA-E018-02 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家J | 船东 | 2026-06-18 | 应急/停泊发电机：确认主配电板恢复供电后应急发电机自动停机 Emergency/Harbor Generator: Kindly confirm that the em/cy gen will stop automaticaly once power from the main swbd will be restored. | B |  |  | 2026-06-22 | Confirm，Technical Protocols 3-4 have been described | 已关闭 | 2026-06-05 | 2026-06-07 | 2026-07-13 | 2026-07-16 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0069 | DEMO-TA-E018-02 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家J | 船东 | 2026-06-20 | 提供各配电板断路器、继电器、接触器、仪表、保护元件等品牌 Kindly provide maker of: Breaker/relays/ contactors/instuments/safety etc for all switchboards | C |  |  | 2026-06-26 | The brand of breaker/relays/ contactors is ABB or siemens,the brand of instrument is Shanghai ziyi | 已关闭 | 2026-06-05 | 2026-06-07 | 2026-07-13 | 2026-07-16 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0070 | DEMO-TA-E018-02 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家J | 船东 | 2026-06-19 | 提供主要配电板示意图/草图 Kindly provide indicative drawing/sketch from all the major switchboards. | B |  |  | 2026-06-22 | We'll submit it in approval drawing stage. | 已关闭 | 2026-06-05 | 2026-06-07 | 2026-07-13 | 2026-07-16 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0071 | DEMO-TA-E018-02 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家J | 船东 | 2026-06-17 | 提供以往项目参考照片 Please provide Indicative photos from past projects | C |  |  | 2026-06-19 | Please refer to the attached file. | 已关闭 | 2026-06-05 | 2026-06-07 | 2026-07-13 | 2026-07-16 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0072 | DEMO-TA-E018-02 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家J | 船东 | 2026-06-18 | 直流电缆颜色：正极红、负极黑 0-6: DC cable: Positive:Red. Negative: Black. | B |  |  | 2026-06-23 | Agree | 已关闭 | 2026-06-05 | 2026-06-07 | 2026-07-13 | 2026-07-16 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0073 | DEMO-TA-E018-02 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家J | 船东 | 2026-06-17 | 确认试验板 24VDC 电源 10-3.: Please confirm 24 VDC supply for test panel | C |  |  | 2026-06-20 | confirm, The DC24V comes from the inner DC power module. | 已关闭 | 2026-06-05 | 2026-06-07 | 2026-07-13 | 2026-07-16 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0074 | DEMO-TA-E018-02 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家J | 船东 | 2026-06-20 | 提供电缆截面清单（内部及外部接线） please provide list for cable size (internal and external wiring) | C |  |  | 2026-06-21 | Flame retardant and halogen free ,Low Smoke.Control line at least 1mm², PLC and other special devices according to equipment requirements, current transformer with not less than 2.5mm². | 已关闭 | 2026-06-05 | 2026-06-07 | 2026-07-13 | 2026-07-16 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0075 | DEMO-TA-E018-03 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家M | 船东 | 2026-06-25 | 220V 及 24V 回路须设微型断路器（MCB） 8-3: Please provide MCB for 220V and 24 V circuits | B |  |  | 2026-06-27 | Agree， 220V AC is provided by the inner transform | 已关闭 | 2026-06-13 | 2026-06-14 | 2026-07-21 | 2026-07-23 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0076 | DEMO-TA-E018-03 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家M | 船东 | 2026-06-27 | 提供各配电板断路器、继电器、接触器、仪表、保护元件等品牌 Kindly provide maker of: Breaker/relays/ contactors/instuments/safety etc for all switchboards | C |  |  | 2026-06-28 | The contactors,thermal overload relay will be ABB/Siemens,the brand of instrument is Shanghai ziyi | 已关闭 | 2026-06-13 | 2026-06-14 | 2026-07-21 | 2026-07-23 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0077 | DEMO-TA-E018-04 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家L | 船东 | 2026-05-30 | 图纸仅使用英文 0-12: Language of the drawings to be only in English | C |  |  | 2026-06-05 | Agree | 已关闭 | 2026-05-20 | 2026-05-23 | 2026-06-18 | 2026-06-21 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0078 | DEMO-TA-E018-04 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家L | 船东 | 2026-05-29 | 所有配电板/箱外壳颜色须为 RAL 9001（奶白色） All switcboard/panels etc external colour to be equivalent to RAL 9001 (cream) | B |  |  | 2026-05-31 | Agree | 已关闭 | 2026-05-20 | 2026-05-23 | 2026-06-18 | 2026-06-21 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0079 | DEMO-TA-E018-04 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家L | 船东 | 2026-05-31 | 提供以往项目参考照片 Please provide Indicative photos from past projects | C |  |  | 2026-06-04 | Please refer to the attached file. | 已关闭 | 2026-05-20 | 2026-05-23 | 2026-06-18 | 2026-06-21 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0080 | DEMO-TA-E018-04 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家L | 船东 | 2026-05-29 | 确认试验板按规格书提供 0–24VDC 及 0–440VAC 可调电源 7-5: Please confirm for test panel 0-24 VDC and 0-440 VAC variable voltage supply according specification | B |  |  | 2026-05-31 | agree，will be provided internally | 已关闭 | 2026-05-20 | 2026-05-23 | 2026-06-18 | 2026-06-21 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0081 | DEMO-TA-E018-05 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家K | 船东 | 2026-06-21 | 所有配电板、分电箱、开关箱、母排等布置图（含仪表、设备、尺寸、标识、原理图）须送审 All switchboards, panels, switch boxes, bus bars etc. layouts with its respective instrumentation, equipment, dimensions, marking and diagrams etc to be be submitted for verification | B |  |  | 2026-06-24 | The equipment outline drawing will be provided to the shipowner and shipowner for confirmation one week after the system drawing is provided by the designer | 已关闭 | 2026-06-16 | 2026-06-15 | 2026-07-14 | 2026-07-20 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0082 | DEMO-TA-E018-05 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家K | 船东 | 2026-06-20 | 详细说明停泊工况下的运行模式 Please more detailed explain operating mode for harbor condition | B |  |  | 2026-06-25 | In harbor mode, power is supplied to the ship by shore power or emergency generators 【船东反馈】Not answered. explain operating mode for harbor condition when the em/cy gen will run as harbor. | 已关闭 | 2026-06-16 | 2026-06-15 | 2026-07-14 | 2026-07-20 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0083 | DEMO-TA-E018-05 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家K | 船东 | 2026-06-20 | 提供电缆截面清单（内部及外部接线） please provide list for cable size (internal and external wiring) | C |  |  | 2026-06-25 | The approved drawing stage will estimate the required cable size and length according to the actual needs , normally, Min. 0.75mm2 for control circuit, Min. 1.5mm2 for power circuit | 已关闭 | 2026-06-16 | 2026-06-15 | 2026-07-14 | 2026-07-20 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0084 | DEMO-TA-E018-05 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家K | 船东 | 2026-06-20 | 不接受记号/热印线号，须采用可打印热缩管或标签 0-9: Wire identification with marker is not acceptable. Printable shrinkable tube, or tags are accepted. | B |  |  | 2026-06-21 | Printed shrink tube or wire labels will be provided | 已关闭 | 2026-06-16 | 2026-06-15 | 2026-07-14 | 2026-07-20 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0085 | DEMO-TA-E018-05 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家K | 船东 | 2026-06-22 | 接触器、热继电器须与断路器同品牌（ABB/西门子），不接受国产品牌 0-23: The contactor,thermal overload relay to be same as the Breakers(ABB/Siemens) for uniformity.No Chinese maker is accepted. | A |  |  | 2026-06-25 | The contactors, thermal overload relays and circuit breakers are branded by ABB | 已关闭 | 2026-06-16 | 2026-06-15 | 2026-07-14 | 2026-07-20 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0086 | DEMO-TA-E018-05 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家K | 船东 | 2026-06-20 | 所有配电板/箱外壳颜色须为 RAL 9001（奶白色） All switcboard/panels etc external colour to be equivalent to RAL 9001 (cream) | B |  |  | 2026-06-22 | Colour of all equipment is RAL 9001 standard (milky white) | 已关闭 | 2026-06-16 | 2026-06-15 | 2026-07-14 | 2026-07-20 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0087 | DEMO-TA-E018-05 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家K | 船东 | 2026-06-20 | 应急/停泊发电机：确认主配电板恢复供电后应急发电机自动停机 Emergency/Harbor Generator: Kindly confirm that the em/cy gen will stop automaticaly once power from the main swbd will be restored. | B |  |  | 2026-06-22 | After restoration of the main net work the emergency generator circuit breaker will be disconnected,than bus-tie circuit breaker will be connected on automatic. | 已关闭 | 2026-06-16 | 2026-06-15 | 2026-07-14 | 2026-07-20 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0088 | DEMO-TA-E018-05 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家K | 船东 | 2026-06-19 | 应急/停泊发电机：说明停泊模式操作程序，澄清短时并车持续时长 Emergency/Harbor Generator: Kindly advise operation sequence on harbor mode.Kindly clarify the short-time synchronous parallel mode. How many seconds will this last? | B |  |  | 2026-06-23 | operation sequence on harbor mode： 1.Put the EG Operating Mode switch in harbor position； 2.Press the start button for the harbor generator； 3.Put the Synchroscope Switch in EG position； 4.Adjust the speed of the harbor generator to make its frequency slightly higher than the busbar； 5.Observe the Synchroscope and press the harbor generator closing button when the LED light rotates to 12 o'clock; 6.Adjust the speed of the harbor generator to transfer the load to the harbor generator, and then press the remote control open button of the transformer circuit breaker on the 440V ASB. Short-time synchronous parallel mode will last about 60 seconds. | 已关闭 | 2026-06-16 | 2026-06-15 | 2026-07-14 | 2026-07-20 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0089 | DEMO-TA-E018-05 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家K | 船东 | 2026-06-20 | 提供各配电板断路器、继电器、接触器、仪表、保护元件等品牌 Kindly provide maker of: Breaker/relays/ contactors/instuments/safety etc for all switchboards | C |  |  | 2026-06-22 | ACB &MCCB&MCB to be of ABB brand. contactors,overcurrent relay to be of ABB brand,meter to be yitai brand. | 已关闭 | 2026-06-16 | 2026-06-15 | 2026-07-14 | 2026-07-20 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0090 | DEMO-TA-E018-05 | 低压配电板及分电箱 LV Switchboard and Power Panel | 厂家K | 船东 | 2026-06-22 | 提供以往项目参考照片 Please provide Indicative photos from past projects | C |  |  | 2026-06-25 | Please refer to the attached file. | 已关闭 | 2026-06-16 | 2026-06-15 | 2026-07-14 | 2026-07-20 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0091 | DEMO-TA-M019-01 | 局部水雾灭火系统 Local Water Mist Fire Fighting System | 厂家N | 船东 | 2026-05-31 | TA 须纳入质保条款 Warranty terms to be included in the Technical agreement | A |  |  | 2026-06-01 | Vendor reply: Meet the requirements | 已关闭 | 2026-05-21 | 2026-05-19 | 2026-06-14 | 2026-06-19 | √ | √ | √ | √ | 中标厂家 | 2026-08-14
TA-0092 | DEMO-TA-M019-01 | 局部水雾灭火系统 Local Water Mist Fire Fighting System | 厂家N | 船东 | 2026-05-29 | 提供全球认可的服务站 Global approved service station to be provided | C |  |  | 2026-05-31 | Vendor reply: Meet the requirements | 已关闭 | 2026-05-21 | 2026-05-19 | 2026-06-14 | 2026-06-19 | √ | √ | √ | √ | 中标厂家 | 2026-08-14
TA-0093 | DEMO-TA-M019-01 | 局部水雾灭火系统 Local Water Mist Fire Fighting System | 厂家N | 船东 | 2026-05-28 | 说明消防泵站所用材料 Please provide more details on fire pump station regarding materials used | C |  |  | 2026-05-31 | Vendor reply: Pipeline material ：304, Frame material：Q235 | 已关闭 | 2026-05-21 | 2026-05-19 | 2026-06-14 | 2026-06-19 | √ | √ | √ | √ | 中标厂家 | 2026-08-14
TA-0094 | DEMO-TA-M019-01 | 局部水雾灭火系统 Local Water Mist Fire Fighting System | 厂家N | 船东 | 2026-05-29 | 提供含安装及检修尺寸、隔离阀、止回阀、滤器等的图纸/草图 In addition to the above. Drawign / sketch with Installation and mainteneance / service dimensions, isolation valves, not-return valves, strainers and so on | B |  |  | 2026-06-06 | Vendor reply: There are currently no relevant drawings available | 已关闭 | 2026-05-21 | 2026-05-19 | 2026-06-14 | 2026-06-19 | √ | √ | √ | √ | 中标厂家 | 2026-08-14
TA-0095 | DEMO-TA-M019-01 | 局部水雾灭火系统 Local Water Mist Fire Fighting System | 厂家N | 船东 | 2026-05-31 | 是否与火灾报警监控系统接口并带地址 1.5 / Page 10: Is there interface with Faire Alarm Monitoring System and have address? | B |  |  | 2026-06-06 | Vendor reply: yes | 已关闭 | 2026-05-21 | 2026-05-19 | 2026-06-14 | 2026-06-19 | √ | √ | √ | √ | 中标厂家 | 2026-08-14
TA-0096 | DEMO-TA-M019-01 | 局部水雾灭火系统 Local Water Mist Fire Fighting System | 厂家N | 船东 | 2026-05-30 | 保护区域及喷头数量在设计和安装阶段核实调整 2 / Page 10: Protected area and quantity of nozzle is subject to verification and adjustment during design and installation stage | B |  |  | 2026-06-03 | Vendor reply: ok | 已关闭 | 2026-05-21 | 2026-05-19 | 2026-06-14 | 2026-06-19 | √ | √ | √ | √ | 中标厂家 | 2026-08-14
TA-0097 | DEMO-TA-M019-01 | 局部水雾灭火系统 Local Water Mist Fire Fighting System | 厂家N | 船东 | 2026-05-28 | 蓄电池间内的探测器、接线箱、警报器等须为防爆（Ex）型 3 / Page 12 / 6, 7, 8: All the detectors, junction boxes, alarm sirens, whatever installed in the battery space to be Ex Type | A |  |  | 2026-05-30 | Vendor reply: Meet the requirements | 已关闭 | 2026-05-21 | 2026-05-19 | 2026-06-14 | 2026-06-19 | √ | √ | √ | √ | 中标厂家 | 2026-08-14
TA-0098 | DEMO-TA-M019-01 | 局部水雾灭火系统 Local Water Mist Fire Fighting System | 厂家N | 船东 | 2026-05-28 | 提供探测器供应商信息 3 / Page 12 / 6, 7, 8: Provide information of the detectors supplier | C |  |  | 2026-05-29 | Vendor reply: System sensor | 已关闭 | 2026-05-21 | 2026-05-19 | 2026-06-14 | 2026-06-19 | √ | √ | √ | √ | 中标厂家 | 2026-08-14
TA-0099 | DEMO-TA-M019-01 | 局部水雾灭火系统 Local Water Mist Fire Fighting System | 厂家N | 船东 | 2026-05-30 | 喷头是否带滤网及防污染外保护盖 3 / Page 13 / 11: Clarify if the nozzles are fitted with strainers (mesh) and outside protection cover against contamination | B |  |  | 2026-06-03 | Vendor reply: Without strainers | 已关闭 | 2026-05-21 | 2026-05-19 | 2026-06-14 | 2026-06-19 | √ | √ | √ | √ | 中标厂家 | 2026-08-14
TA-0100 | DEMO-TA-M019-01 | 局部水雾灭火系统 Local Water Mist Fire Fighting System | 厂家N | 船东 | 2026-05-31 | 备注栏文字译成英文 3 / Page 14 / 12:Text in Remark column. Translate into English | C |  |  | 2026-06-08 | Vendor reply: ok | 已关闭 | 2026-05-21 | 2026-05-19 | 2026-06-14 | 2026-06-19 | √ | √ | √ | √ | 中标厂家 | 2026-08-14
TA-0101 | DEMO-TA-M019-02 | 局部水雾灭火系统 Local Water Mist Fire Fighting System | 厂家O | 船东 | 2026-11-05 | 水雾喷头材质应为 SUS316 而非 304 Water mist nozzles to be of SUS316 instead of 304 | A |  |  |  |  | 待回复 | 2026-10-06 | 2026-10-07 | 2026-11-20
TA-0102 | DEMO-TA-M019-02 | 局部水雾灭火系统 Local Water Mist Fire Fighting System | 厂家O | 船东 | 2026-10-27 | 提供泵组草图/图纸（含尺寸、检修空间及附件） 3.1.1 / Page 12: Provide sketch / drawing of the pump unit with dimensions (including service and maitenance) and fittings | B |  |  | 2026-11-01 | Vendor reply: If it is reflected in our company's winning bid drawings in the future | 已关闭 | 2026-10-06 | 2026-10-07 | 2026-11-20
TA-0103 | DEMO-TA-M019-02 | 局部水雾灭火系统 Local Water Mist Fire Fighting System | 厂家O | 船东 | 2026-11-04 | 流程图中文字译成英文 3.1.1 / Page 12: Translate texts in the diaram into English | C |  |  |  |  | 待回复 | 2026-10-06 | 2026-10-07 | 2026-11-20
TA-0104 | DEMO-TA-M019-02 | 局部水雾灭火系统 Local Water Mist Fire Fighting System | 厂家O | 船东 | 2026-10-28 | 电气接口无图，提供与火灾报警监控、IAS、VDR 等系统的接口信息 3.2.1 / Electrical Interface / Page 14: there is no diagram. Please provide information on interface with other systems: Fire Alarm an Monitoring, IAS, VDR etc. | B |  |  | 2026-11-01 | Vendor reply: If our company confirms in the winning bid drawings in the future | 已关闭 | 2026-10-06 | 2026-10-07 | 2026-11-20
TA-0105 | DEMO-TA-M019-02 | 局部水雾灭火系统 Local Water Mist Fire Fighting System | 厂家O | 船东 | 2026-10-28 | 试验及吹扫接口应设止回阀 Scope of Supply / Page 15 / 3-11: There should be non-return valve for testing and blowing connection | B |  |  | 2026-11-01 | Vendor reply: This valve also serves as a testing and blowing function | 已认可待落实 | 2026-10-06 | 2026-10-07 | 2026-11-20
TA-0106 | DEMO-TA-M019-02 | 局部水雾灭火系统 Local Water Mist Fire Fighting System | 厂家O | 船东 | 2026-10-28 | 澄清喷头与管路的连接方式（焊接还是螺纹） Scope of Supply / Page 15 / 12 / Nozzle: Welding base' Please clarify how nozzle to be connected to the pipe (by welding), not threaded? | C |  |  | 2026-10-30 | Vendor reply: The nozzle and welding seat are threaded connections, and the welding seat is butt welded to the pipeline | 已回复待确认 | 2026-10-06 | 2026-10-07 | 2026-11-20
TA-0107 | DEMO-TA-M019-02 | 局部水雾灭火系统 Local Water Mist Fire Fighting System | 厂家O | 船东 | 2026-10-29 | 喷头是否带滤器 Scope of Supply / Page 15 / 12 / Nozzle: Is nozzle fitted with strainer? | C |  |  | 2026-11-03 | Vendor reply: The nozzle is equipped with a filter inside | 已关闭 | 2026-10-06 | 2026-10-07 | 2026-11-20
TA-0108 | DEMO-TA-M019-02 | 局部水雾灭火系统 Local Water Mist Fire Fighting System | 厂家O | 船东 | 2026-10-29 | 喷头是否配临时保护帽 Scope of Supply / Page 15 / 12 / Nozzle: Is nozzle supplied with temporary protection cap? | C |  |  | 2026-10-31 | Vendor reply: not configured | 已回复待确认 | 2026-10-06 | 2026-10-07 | 2026-11-20
TA-0109 | DEMO-TA-M019-02 | 局部水雾灭火系统 Local Water Mist Fire Fighting System | 厂家O | 船东 | 2026-10-29 | 蓄电池间内的探测器、接线箱、警报器等须为防爆（Ex）型 Scope of Supply / Page 16 / 19-21: All detectors, alarm lights, junction boxes whatever installed in the battery room should be Ex Type | A |  |  | 2026-11-01 | Vendor reply: Known and informed | 已认可待落实 | 2026-10-06 | 2026-10-07 | 2026-11-20
TA-0110 | DEMO-TA-M019-02 | 局部水雾灭火系统 Local Water Mist Fire Fighting System | 厂家O | 船东 | 2026-10-30 | 告知探测器及手动报警按钮厂家 Scope of Supply / Page 16 / 19-21: Please let us know the detector and manual call points' manufacturer | C |  |  | 2026-11-01 | Vendor reply: Jiangsu Wuxi Blue Sky | 已关闭 | 2026-10-06 | 2026-10-07 | 2026-11-20
TA-0111 | DEMO-TA-M019-02 | 局部水雾灭火系统 Local Water Mist Fire Fighting System | 厂家O | 船东 | 2026-10-30 | 澄清探测器及手动报警按钮是否均为独立地址 Scope of Supply / Page 16 / 19-21: Clarify if all detector and manual call point have individaul address | C |  |  | 2026-11-04 | Vendor reply: There is a separate address | 已关闭 | 2026-10-06 | 2026-10-07 | 2026-11-20
TA-0112 | DEMO-TA-M019-02 | 局部水雾灭火系统 Local Water Mist Fire Fighting System | 厂家O | 船东 | 2026-10-30 | 提供控制箱草图 Provide sketches of control panels | B |  |  | 2026-11-02 | Vendor reply: If our company confirms in the winning bid drawings in the future | 已回复待确认 | 2026-10-06 | 2026-10-07 | 2026-11-20
TA-0113 | DEMO-TA-M020-01 | CO2 灭火系统 CO2 Fire Fighting System | 厂家N | 船东 | 2026-07-14 | 管材须明确为 SS316L Pipe material to be specified ie SS316L | A |  |  | 2026-07-19 | Vendor reply: Already noted | 已关闭 | 2026-07-08 | 2026-07-08 | 2026-08-09 | 2026-08-12 | √ | √ | √ | √ | 中标厂家 | 2026-10-05
TA-0114 | DEMO-TA-M020-01 | CO2 灭火系统 CO2 Fire Fighting System | 厂家N | 船东 | 2026-07-16 | 确认售后服务可全球覆盖 After sales support to be confirmed that could provide global coverage | C |  |  | 2026-07-18 | Vendor reply: Already noted | 已关闭 | 2026-07-08 | 2026-07-08 | 2026-08-09 | 2026-08-12 | √ | √ | √ | √ | 中标厂家 | 2026-10-05
TA-0115 | DEMO-TA-M020-01 | CO2 灭火系统 CO2 Fire Fighting System | 厂家N | 船东 | 2026-07-16 | 管路连接方式须与合同规格书一致 Pipe connection to be aligned with contract specification | B |  |  | 2026-07-20 | Vendor reply: Meet the requirements | 已关闭 | 2026-07-08 | 2026-07-08 | 2026-08-09 | 2026-08-12 | √ | √ | √ | √ | 中标厂家 | 2026-10-05
TA-0116 | DEMO-TA-M020-01 | CO2 灭火系统 CO2 Fire Fighting System | 厂家N | 船东 | 2026-07-16 | 提供远程释放柜详细图纸 Please provide more detailed dwg for remote release cabinet | B |  |  | 2026-07-19 | Vendor reply: pls see the attached 1 drawing. | 已关闭 | 2026-07-08 | 2026-07-08 | 2026-08-09 | 2026-08-12 | √ | √ | √ | √ | 中标厂家 | 2026-10-05
TA-0117 | DEMO-TA-M020-01 | CO2 灭火系统 CO2 Fire Fighting System | 厂家N | 船东 | 2026-07-14 | 缺少厨房烟道（Galley duct）计算 Calculation for galley duct missing. | B |  |  | 2026-07-19 | Vendor reply: No parameters for galley duct | 已关闭 | 2026-07-08 | 2026-07-08 | 2026-08-09 | 2026-08-12 | √ | √ | √ | √ | 中标厂家 | 2026-10-05
TA-0118 | DEMO-TA-M020-01 | CO2 灭火系统 CO2 Fire Fighting System | 厂家N | 船东 | 2026-07-14 | 详细说明各保护区（蓄电池间、应急发电机间、厨房、主配电板间）预警/释放报警、风机泵停机、失电报警等功能 Please provide more detailed information about prealarm and release alarms and ventilation/pumps stop functions, power fail alarm etc, for each systems (battery room, EDG room, galley, MSB room) | B |  |  | 2026-07-15 | Vendor reply: Meet the requirements | 已关闭 | 2026-07-08 | 2026-07-08 | 2026-08-09 | 2026-08-12 | √ | √ | √ | √ | 中标厂家 | 2026-10-05
TA-0119 | DEMO-TA-M020-01 | CO2 灭火系统 CO2 Fire Fighting System | 厂家N | 船东 | 2026-07-14 | 提供含远程释放的系统总图 Please provide systems general diagram with remote rellease | B |  |  | 2026-07-17 | Vendor reply: pls see the attached 2 drawing. | 已关闭 | 2026-07-08 | 2026-07-08 | 2026-08-09 | 2026-08-12 | √ | √ | √ | √ | 中标厂家 | 2026-10-05
TA-0120 | DEMO-TA-M020-02 | CO2 灭火系统 CO2 Fire Fighting System | 厂家O | 船东 | 2026-06-02 | 管路连接方式须与合同规格书一致 Pipe connection to be aligned with contract specification | B |  |  | 2026-06-03 | Vendor reply: Meet regulatory requirements | 已关闭 | 2026-05-22 | 2026-05-24 | 2026-07-02 | 2026-07-01 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0121 | DEMO-TA-M020-02 | CO2 灭火系统 CO2 Fire Fighting System | 厂家O | 船东 | 2026-06-04 | 「Kitchen flue」应按合同规格书改称「Galley duct」 3.2 'Kitchen flue' to be reffered as 'Galley duct' as per contract specification | C |  |  | 2026-06-08 | Vendor reply: We have been informed that if our company wins the bid in the future, we can provide suggestions for changes in the drawings | 已关闭 | 2026-05-22 | 2026-05-24 | 2026-07-02 | 2026-07-01 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0122 | DEMO-TA-M020-02 | CO2 灭火系统 CO2 Fire Fighting System | 厂家O | 船东 | 2026-06-02 | 提供远程释放柜详细图纸 Please provide more detailed dwg for remote release cabinet | B |  |  | 2026-06-05 | Vendor reply: If it is reflected in our company's winning bid drawings in the future | 已关闭 | 2026-05-22 | 2026-05-24 | 2026-07-02 | 2026-07-01 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0123 | DEMO-TA-M020-02 | CO2 灭火系统 CO2 Fire Fighting System | 厂家O | 船东 | 2026-06-01 | 缺少厨房烟道（Galley duct）计算 Calculation for galley duct missing. | B |  |  | 2026-06-04 | Vendor reply: Due to the temporary lack of pipeline capacity, the kitchen pipeline is configured with a 10L bottle set based on our company's experience | 已关闭 | 2026-05-22 | 2026-05-24 | 2026-07-02 | 2026-07-01 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0124 | DEMO-TA-M020-02 | CO2 灭火系统 CO2 Fire Fighting System | 厂家O | 船东 | 2026-06-02 | 详细说明各保护区（蓄电池间、应急发电机间、厨房、主配电板间）预警/释放报警、风机泵停机、失电报警等功能 Please provide more detailed information about prealarm and release alarms and ventilation/pumps stop functions, power fail alarm etc, for each systems (battery room, EDG room, galley, MSB room) | B |  |  | 2026-06-03 | Vendor reply: If it is reflected in our company's winning bid drawings in the future | 已关闭 | 2026-05-22 | 2026-05-24 | 2026-07-02 | 2026-07-01 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0125 | DEMO-TA-M020-02 | CO2 灭火系统 CO2 Fire Fighting System | 厂家O | 船东 | 2026-06-03 | 提供含远程释放的系统总图 Please provide systems general diagram with remote rellease | B |  |  | 2026-06-09 | Vendor reply: If it is reflected in our company's winning bid drawings in the future | 已关闭 | 2026-05-22 | 2026-05-24 | 2026-07-02 | 2026-07-01 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0126 | DEMO-TA-M022-03 | 压力水柜及热水柜 Hydrophore Tank & Calorifier | 厂家P | 船东 | 2026-10-31 | 提供主要部件品牌（泵、压力开关、涂料规格及膜厚、安全阀、温度计、压力表/变送器、液位及压力开关等） Please provide maker from all the main components. See list (but not limited only to those):Pumps,Pressostats,Exact Paint specification with microns and paint maker,safety valves,thermometers,pressure gauges & transmitters, Level and press switches etc. | C |  |  |  |  | 待回复 | 2026-09-30 | 2026-10-04 | 2026-11-13 |  | √ | 缺 | √ |  | 中标厂家
TA-0127 | DEMO-TA-M022-03 | 压力水柜及热水柜 Hydrophore Tank & Calorifier | 厂家P | 船东 | 2026-10-31 | 热水柜须能达到至少 70℃（MLC），柜体及管路保温应包含在内 Calorifier unit should be able to reach at least 70degrees Celsious according to MLC rules. So insulation of the tank and pipes should be included. | A |  |  |  |  | 待回复 | 2026-09-30 | 2026-10-04 | 2026-11-13 |  | √ | 缺 | √ |  | 中标厂家
TA-0128 | DEMO-TA-M022-03 | 压力水柜及热水柜 Hydrophore Tank & Calorifier | 厂家P | 船东 | 2026-10-28 | 说明碳钢饮用水管的防锈处理方式 Page 10: Clarify what treatment is applied for the potable water pipes (carbon steel material) to prevent rust | B |  |  | 2026-10-31 | Vendor reply: Drinking water tank paint | 已回复待确认 | 2026-09-30 | 2026-10-04 | 2026-11-13 |  | √ | 缺 | √ |  | 中标厂家
TA-0129 | DEMO-TA-M022-03 | 压力水柜及热水柜 Hydrophore Tank & Calorifier | 厂家P | 船东 | 2026-10-29 | 液位计是否带隔离阀，表中为何未标数量 Let us know if the level gauge are fitted with isolation valves. And why they are not marked with quantity in the tables | C |  |  | 2026-11-02 | Vendor reply: With 2pc isolation valves | 已关闭 | 2026-09-30 | 2026-10-04 | 2026-11-13 |  | √ | 缺 | √ |  | 中标厂家
TA-0130 | DEMO-TA-M022-03 | 压力水柜及热水柜 Hydrophore Tank & Calorifier | 厂家P | 船东 | 2026-10-29 | 提供人孔净尺寸 Provide clear size of the manholes | C |  |  | 2026-11-03 | Vendor reply: DN400 | 已关闭 | 2026-09-30 | 2026-10-04 | 2026-11-13 |  | √ | 缺 | √ |  | 中标厂家
TA-0131 | DEMO-TA-M022-03 | 压力水柜及热水柜 Hydrophore Tank & Calorifier | 厂家P | 船东 | 2026-10-29 | 确认安全阀已由厂家试验、整定并铅封 Please verify if safety valves are tested, set for required pressure and sealed by the manufacturer | C |  |  | 2026-11-03 | Vendor reply: Yes | 已认可待落实 | 2026-09-30 | 2026-10-04 | 2026-11-13 |  | √ | 缺 | √ |  | 中标厂家
TA-0132 | DEMO-TA-M022-03 | 压力水柜及热水柜 Hydrophore Tank & Calorifier | 厂家P | 船东 | 2026-10-30 | 澄清是否提供 IAS 接口 Clarify if IAS interfaceis provided | C |  |  | 2026-11-03 | Vendor reply: No | 已关闭 | 2026-09-30 | 2026-10-04 | 2026-11-13 |  | √ | 缺 | √ |  | 中标厂家
TA-0133 | DEMO-TA-M022-03 | 压力水柜及热水柜 Hydrophore Tank & Calorifier | 厂家P | 船东 | 2026-11-03 | 提供控制箱草图及报警、指示清单 Provide sketch of the control boxes, alarm and indication list | B |  |  |  |  | 待回复 | 2026-09-30 | 2026-10-04 | 2026-11-13 |  | √ | 缺 | √ |  | 中标厂家
TA-0134 | DEMO-TA-M002-01 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家Q | 船东 | 2026-10-25 | 确认发动机能否使用 FAME/HVO 生物柴油 Kindly confirm that engine is capable of operating with FAME or HVO Biodiesel. | A |  |  | 2026-10-31 | Can use B20 biodiesel blend fuel | 已认可待落实 | 2026-10-04 | 2026-10-07 | 2026-11-23
TA-0135 | DEMO-TA-M002-01 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家Q | 船东 | 2026-10-28 | 请提供发电机（电机）厂家 Please provide Generator Maker. | C |  |  |  |  | 待回复 | 2026-10-04 | 2026-10-07 | 2026-11-23
TA-0136 | DEMO-TA-M002-01 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家Q | 船东 | 2026-10-25 | 滑油滤器应为双联，请确认 LO Filter should be double, please confirm | A |  |  | 2026-10-29 | Dual non switchable type | 已关闭 | 2026-10-04 | 2026-10-07 | 2026-11-23
TA-0137 | DEMO-TA-M002-01 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家Q | 船东 | 2026-10-26 | 燃油滤器应为双联，请确认 FO Filter, should be double, please confirm | A |  |  | 2026-10-27 | Dual non switchable type | 已关闭 | 2026-10-04 | 2026-10-07 | 2026-11-23
TA-0138 | DEMO-TA-M002-01 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家Q | 船东 | 2026-10-26 | 提供调速器供应商信息 Provide information about Governor supplier | C |  |  | 2026-11-02 | The governor maker: Cummins | 已关闭 | 2026-10-04 | 2026-10-07 | 2026-11-23
TA-0139 | DEMO-TA-M002-01 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家Q | 船东 | 2026-10-26 | 提供 AVR（自动调压器）供应商信息 Provide information about AVR supplier | C |  |  | 2026-10-31 | The AVR is provide by generator maker | 已回复待确认 | 2026-10-04 | 2026-10-07 | 2026-11-23
TA-0140 | DEMO-TA-M002-01 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家Q | 船东 | 2026-10-27 | 澄清滑油低压、冷却水高温停机在应急工况下是否生效 Please clarify if lub oil pressure low and cooling water tem. high shutdowns will also apply in emergency conditions | B |  |  | 2026-10-29 | These two shutdown functions are only effective in parking mode | 已认可待落实 | 2026-10-04 | 2026-10-07 | 2026-11-23
TA-0141 | DEMO-TA-M002-01 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家Q | 船东 | 2026-10-27 | 明确与 IAS 的接口（报警及指示） Please specify interface with IAS (alarms and indication) | B |  |  | 2026-11-01 | Confirmation of Relevant Information Recognition Data Stage | 已关闭 | 2026-10-04 | 2026-10-07 | 2026-11-23
TA-0142 | DEMO-TA-M002-01 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家Q | 船东 | 2026-10-27 | 提供机组主尺度（含检修维护空间） Please include principal dimentions of the Gen-Set (including service and mentenance) | A |  |  | 2026-10-30 | Please find attached 1 the outline drawing of the unit for reference. The final drawing shall be subject to the approved materials | 已回复待确认 | 2026-10-04 | 2026-10-07 | 2026-11-23
TA-0143 | DEMO-TA-M002-01 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家Q | 船东 | 2026-10-28 | 提供燃油/滑油/冷却水/排气系统 P&ID 图 Provide P&ID diagrams for all (FO, LO, CW, Exhaust) systems | B |  |  | 2026-10-30 | Please find attached 2 the P&ID diagram | 已认可待落实 | 2026-10-04 | 2026-10-07 | 2026-11-23
TA-0144 | DEMO-TA-M002-01 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家Q | 船东 | 2026-11-05 | 提供控制箱布置草图 Provide Control Panel layout sketch | B |  |  |  |  | 待回复 | 2026-10-04 | 2026-10-07 | 2026-11-23
TA-0145 | DEMO-TA-M002-01 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家Q | 船东 | 2026-10-28 | 是否具备测试模式 Please let us know if there is a test mode | C |  |  | 2026-10-30 | There is no testing mode | 已关闭 | 2026-10-04 | 2026-10-07 | 2026-11-23
TA-0146 | DEMO-TA-M002-01 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家Q | 船东 | 2026-10-29 | 测试/停泊/应急模式之间是否设选择开关 Is there selector switch between the modes test (if any), harbour, emergency modes | C |  |  | 2026-11-02 | The control box has a harbor/emergency mode switch | 已关闭 | 2026-10-04 | 2026-10-07 | 2026-11-23
TA-0147 | DEMO-TA-M002-01 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家Q | 船东 | 2026-10-30 | 提供售后服务网络 General. Please provide after-sales service network | C |  |  |  |  | 待回复 | 2026-10-04 | 2026-10-07 | 2026-11-23
TA-0148 | DEMO-TA-M002-02 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家R | 船东 | 2026-06-09 | 确认发动机能否使用 FAME/HVO 生物柴油 Kindly confirm that engine is capable of operating with FAME or HVO Biodiesel. | A |  |  | 2026-06-10 | Vendor reply: FAME: ONLY B20 (see the attached files), HVO:100% | 已关闭 | 2026-05-28 | 2026-05-29 | 2026-07-01 | 2026-07-03 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0149 | DEMO-TA-M002-02 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家R | 船东 | 2026-06-07 | 提供调速器供应商信息 Section A / Page 11: Provide information about Governor supplier | C |  |  | 2026-06-11 | Vendor reply: EFC Electric type Governor made by Cummins Chongqing (CCEC） | 已关闭 | 2026-05-28 | 2026-05-29 | 2026-07-01 | 2026-07-03 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0150 | DEMO-TA-M002-02 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家R | 船东 | 2026-06-06 | 滑油滤器应为双联，请确认 Section C / Scope of Supply / 1.3.2 / Page 15: LO Filter should be double, please confirm | A |  |  | 2026-06-08 | Vendor reply: Cummins no supply | 已关闭 | 2026-05-28 | 2026-05-29 | 2026-07-01 | 2026-07-03 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0151 | DEMO-TA-M002-02 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家R | 船东 | 2026-06-09 | 燃油滤器应为双联，请确认 Section C / Scope of Supply / 1.4.1 / Page 15: FO Filter, should be double, please confirm | A |  |  | 2026-06-15 | Vendor reply: Fuel water separator（stage one) is double. | 已关闭 | 2026-05-28 | 2026-05-29 | 2026-07-01 | 2026-07-03 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0152 | DEMO-TA-M002-02 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家R | 船东 | 2026-06-09 | 澄清尿素日用柜材质（是否不锈钢） Section C Scope of Supply / 1.6.2 / Page 19: Clarify material of the Urea Daily tank. SUS? | C |  |  | 2026-06-11 | Vendor reply: Stainless Steel 304L | 已关闭 | 2026-05-28 | 2026-05-29 | 2026-07-01 | 2026-07-03 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0153 | DEMO-TA-M002-02 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家R | 船东 | 2026-06-07 | 提供 AVR（自动调压器）供应商信息 Section C Scope of Supply / 2 / Page 20: Provide information about AVR supplier | C |  |  | 2026-06-10 | Vendor reply: AVR D350 made by Leroy Somer | 已关闭 | 2026-05-28 | 2026-05-29 | 2026-07-01 | 2026-07-03 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0154 | DEMO-TA-M002-02 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家R | 船东 | 2026-06-07 | 停泊/测试模式下是否设滑油低压、冷却水高温停机 Section C Scope of Supply / 3.3 / Page 20: Are there lub oil pressure low, cooling water temp. high shut downs on harbour and test modes? | B |  |  | 2026-06-08 | Vendor reply: On harbour and self-check modes. | 已关闭 | 2026-05-28 | 2026-05-29 | 2026-07-01 | 2026-07-03 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0155 | DEMO-TA-M002-02 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家R | 船东 | 2026-06-09 | 质保条款需译成英文 11. Warranty / 11.2 / Page 22: Translate into English | C |  |  | 2026-06-12 | Vendor reply: 11.2 is a clerical error, the content is 11.1 Chinese | 已关闭 | 2026-05-28 | 2026-05-29 | 2026-07-01 | 2026-07-03 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0156 | DEMO-TA-M002-02 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家R | 船东 | 2026-06-07 | 质保条款需译成英文 11. Warranty / 11.4 / Page 22: Translate into English | C |  |  | 2026-06-08 | Vendor reply: 11.4 is a clerical error, the content is 11.3 Chinese | 已关闭 | 2026-05-28 | 2026-05-29 | 2026-07-01 | 2026-07-03 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0157 | DEMO-TA-M002-02 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家R | 船东 | 2026-06-07 | 厂家调试服务范围是否同时包含机组和 SCR 12 / FAT / Page 23: Does the scope of commissioninig works and services provided by the supplier include both Gen-Set and SCR? | A |  |  | 2026-06-09 | Vendor reply: Yes | 已关闭 | 2026-05-28 | 2026-05-29 | 2026-07-01 | 2026-07-03 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0158 | DEMO-TA-M002-02 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家R | 船东 | 2026-06-06 | 提供机组主尺度（含检修维护空间） Please include principal dimentions of the Gen-Set (including service and mentenance) | A |  |  | 2026-06-09 | Vendor reply: pls see attached 1, only for reference. | 已关闭 | 2026-05-28 | 2026-05-29 | 2026-07-01 | 2026-07-03 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0159 | DEMO-TA-M002-02 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家R | 船东 | 2026-06-08 | 提供燃油/滑油/冷却水/排气系统 P&ID 图 Provide P&ID diagrams for all (FO, LO, CW, Exhaust) systems | B |  |  | 2026-06-10 | Vendor reply: pls see attached 2, only for reference. | 已关闭 | 2026-05-28 | 2026-05-29 | 2026-07-01 | 2026-07-03 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0160 | DEMO-TA-M002-02 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家R | 船东 | 2026-06-09 | 提供控制箱布置草图 Provide Control Panel layout sketch | B |  |  | 2026-06-11 | Vendor reply: pls see attached 3, only for reference. | 已关闭 | 2026-05-28 | 2026-05-29 | 2026-07-01 | 2026-07-03 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0161 | DEMO-TA-M002-02 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家R | 船东 | 2026-06-08 | 是否具备测试模式 Please let us know if there is a test mode | C |  |  | 2026-06-12 | Vendor reply: The local control box has a self-check mode without starting engine, and the test mode is generally the function of the ESB. | 已关闭 | 2026-05-28 | 2026-05-29 | 2026-07-01 | 2026-07-03 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0162 | DEMO-TA-M002-02 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家R | 船东 | 2026-06-08 | 提供售后服务网络 General. Please provide after-sales service network | C |  |  | 2026-06-10 | Vendor reply: OK.see the attached 4 files. | 已关闭 | 2026-05-28 | 2026-05-29 | 2026-07-01 | 2026-07-03 |  |  |  |  | 未中标厂家（定标前澄清意见）
TA-0163 | DEMO-TA-M002-03 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家S | 船东 | 2026-10-28 | 确认发动机能否使用 FAME/HVO 生物柴油 Kindly confirm that engine is capable of operating with FAME or HVO Biodiesel. | A |  |  | 2026-10-30 | Vendor reply: Please refer to Cummins fuel specifications“Fuels for Cummins® Engines-Bulletin_3379001-21” | 已关闭 | 2026-10-03 | 2026-10-05 | 2026-11-18
TA-0164 | DEMO-TA-M002-03 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家S | 船东 | 2026-10-28 | 提供调速器供应商信息 Section A / Page 11: Provide information about Governor supplier | C |  |  | 2026-11-02 | Vendor reply: Governor supplier is CUMMINS，Type is EFC | 已关闭 | 2026-10-03 | 2026-10-05 | 2026-11-18
TA-0165 | DEMO-TA-M002-03 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家S | 船东 | 2026-10-28 | 滑油滤器应为双联，请确认 Section C / Scope of Supply / 1.3.2 / Page 16: LO Filter should be double, please confirm | A |  |  | 2026-10-31 | Vendor reply: Confirmed | 已认可待落实 | 2026-10-03 | 2026-10-05 | 2026-11-18
TA-0166 | DEMO-TA-M002-03 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家S | 船东 | 2026-10-30 | 燃油滤器应为双联，请确认 Section C / Scope of Supply / 1.4.1 / Page 16: FO Filter, should be double, please confirm | A |  |  |  |  | 待回复 | 2026-10-03 | 2026-10-05 | 2026-11-18
TA-0167 | DEMO-TA-M002-03 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家S | 船东 | 2026-10-29 | 提供 AVR（自动调压器）供应商信息 Section C / Scope of Supply / 2.1 / Page 17: Provide information about AVR supplier | C |  |  | 2026-10-31 | Vendor reply: Governor supplier is CUMMINS Stamford，Type is MX321 | 已回复待确认 | 2026-10-03 | 2026-10-05 | 2026-11-18
TA-0168 | DEMO-TA-M002-03 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家S | 船东 | 2026-11-02 | 停泊/测试模式下是否设滑油低压、冷却水高温停机 Section C / Scope of Supply / 3.3 / Page 18: Are there lub oil pressure low, cooling water temp. high shut downs on harbour and test modes? | B |  |  |  |  | 待回复 | 2026-10-03 | 2026-10-05 | 2026-11-18
TA-0169 | DEMO-TA-M002-03 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家S | 船东 | 2026-10-30 | 厂家调试服务范围是否同时包含机组和 SCR Section C / Scope of Supply / 7 / Page 19: Does the scope of commissioninig works and services provided by the supplier include both Gen-Set and SCR? | A |  |  | 2026-11-01 | Vendor reply: Yes | 已认可待落实 | 2026-10-03 | 2026-10-05 | 2026-11-18
TA-0170 | DEMO-TA-M002-03 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家S | 船东 | 2026-10-30 | 提供机组主尺度（含检修维护空间） Please include principal dimentions of the Gen-Set (including service and mentenance space) | A |  |  | 2026-11-01 | Vendor reply: L5470*B2120*H2750mm，Service and mentenance space should not exceed the maximum external dimensions of the unit | 已回复待确认 | 2026-10-03 | 2026-10-05 | 2026-11-18
TA-0171 | DEMO-TA-M002-03 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家S | 船东 | 2026-10-30 | 提供燃油/滑油/冷却水/排气系统 P&ID 图 Provide P&ID diagrams for all (FO, LO, CW, Exhaust) systems | B |  |  | 2026-11-05 | Vendor reply: Please refer to the attached 1 PID | 已关闭 | 2026-10-03 | 2026-10-05 | 2026-11-18
TA-0172 | DEMO-TA-M002-03 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家S | 船东 | 2026-11-05 | 提供控制箱布置草图 Provide Control Panel layout sketch | B |  |  |  |  | 待回复 | 2026-10-03 | 2026-10-05 | 2026-11-18
TA-0173 | DEMO-TA-M002-03 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家S | 船东 | 2026-10-31 | 是否具备测试模式 Please let us know if there is a test mode | C |  |  |  |  | 待回复 | 2026-10-03 | 2026-10-05 | 2026-11-18
TA-0174 | DEMO-TA-M002-03 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家S | 船东 | 2026-10-31 | 提供售后服务网络 General. Please provide after-sales service network | C |  |  |  |  | 待回复 | 2026-10-03 | 2026-10-05 | 2026-11-18
TA-0175 | DEMO-TA-M002-04 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家T | 船东 | 2026-06-01 | 确认发动机能否使用 FAME/HVO 生物柴油 Kindly confirm that engine is capable of operating with FAME or HVO Biodiesel. | A |  |  | 2026-06-03 | Vendor reply: Confirm. | 已关闭 | 2026-05-19 | 2026-05-21 | 2026-06-18 | 2026-06-21 | √ | √ | √ | √ | 中标厂家。6.13提供了SCR资料，6.24提供了SCR电控接口图 | 2026-08-13
TA-0176 | DEMO-TA-M002-04 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家T | 船东 | 2026-06-01 | 提供调速器供应商信息 Section A / Tech. Specification Page 12:Provide information about Governor supplier | C |  |  | 2026-06-03 | Vendor reply: Cummins | 已关闭 | 2026-05-19 | 2026-05-21 | 2026-06-18 | 2026-06-21 | √ | √ | √ | √ | 中标厂家。6.13提供了SCR资料，6.24提供了SCR电控接口图 | 2026-08-13
TA-0177 | DEMO-TA-M002-04 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家T | 船东 | 2026-05-31 | 滑油滤器应为双联，请确认 Section C/ Scope of Supply / 1.3.2 / Page 16: LO Filter should be double, please confirm | A |  |  | 2026-06-01 | Vendor reply: Confirm. | 已关闭 | 2026-05-19 | 2026-05-21 | 2026-06-18 | 2026-06-21 | √ | √ | √ | √ | 中标厂家。6.13提供了SCR资料，6.24提供了SCR电控接口图 | 2026-08-13
TA-0178 | DEMO-TA-M002-04 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家T | 船东 | 2026-06-02 | 燃油滤器应为双联，请确认 Section C/ Scope of Supply / 1.4.1 / Page 16: FO Filter, should be double, please confirm | A |  |  | 2026-06-05 | Vendor reply: Confirm. | 已关闭 | 2026-05-19 | 2026-05-21 | 2026-06-18 | 2026-06-21 | √ | √ | √ | √ | 中标厂家。6.13提供了SCR资料，6.24提供了SCR电控接口图 | 2026-08-13
TA-0179 | DEMO-TA-M002-04 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家T | 船东 | 2026-06-02 | 提供 AVR（自动调压器）供应商信息 Section C/ Scope of Supply / 2 / Page 17: Provide information about AVR supplier | C |  |  | 2026-06-05 | Vendor reply: Stamford | 已关闭 | 2026-05-19 | 2026-05-21 | 2026-06-18 | 2026-06-21 | √ | √ | √ | √ | 中标厂家。6.13提供了SCR资料，6.24提供了SCR电控接口图 | 2026-08-13
TA-0180 | DEMO-TA-M002-04 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家T | 船东 | 2026-06-03 | 停泊/测试模式下是否设滑油低压、冷却水高温停机 Section C/ Scope of Supply / 3.3 / Page 18: Are there lub oil pressure low, cooling water temp. high shut downs on harbour and test modes? | B |  |  | 2026-06-08 | Vendor reply: Yes,there are. | 已关闭 | 2026-05-19 | 2026-05-21 | 2026-06-18 | 2026-06-21 | √ | √ | √ | √ | 中标厂家。6.13提供了SCR资料，6.24提供了SCR电控接口图 | 2026-08-13
TA-0181 | DEMO-TA-M002-04 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家T | 船东 | 2026-05-31 | 厂家调试服务范围是否同时包含机组和 SCR Section C/ Scope of Supply / 6 / Page 19: Does the scope of commissioninig works and services provided by the supplier include both Gen-Set and SCR? | A |  |  | 2026-06-01 | Vendor reply: Yes | 已关闭 | 2026-05-19 | 2026-05-21 | 2026-06-18 | 2026-06-21 | √ | √ | √ | √ | 中标厂家。6.13提供了SCR资料，6.24提供了SCR电控接口图 | 2026-08-13
TA-0182 | DEMO-TA-M002-04 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家T | 船东 | 2026-06-01 | 澄清 SCR（IDENOx）供货是否含喷射喷嘴 SCR Supply Scope / IDENOx / Page 24: Clarify if the injection nozzle is included. | A |  |  | 2026-06-04 | Vendor reply: Yes | 已关闭 | 2026-05-19 | 2026-05-21 | 2026-06-18 | 2026-06-21 | √ | √ | √ | √ | 中标厂家。6.13提供了SCR资料，6.24提供了SCR电控接口图 | 2026-08-13
TA-0183 | DEMO-TA-M002-04 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家T | 船东 | 2026-05-31 | 提供机组主尺度（含检修维护空间） Please include principal dimentions of the Gen-Set (including service and mentenance) | A |  |  | 2026-06-03 | Vendor reply: 5350mm*1700mm*2150mm, TO BE CONFIRMED IN APPROVAL DRAWING. Maintenance space is not less than 800MM. | 已关闭 | 2026-05-19 | 2026-05-21 | 2026-06-18 | 2026-06-21 | √ | √ | √ | √ | 中标厂家。6.13提供了SCR资料，6.24提供了SCR电控接口图 | 2026-08-13
TA-0184 | DEMO-TA-M002-04 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家T | 船东 | 2026-06-02 | 提供燃油/滑油/冷却水/排气系统 P&ID 图 Provide P&ID diagrams for all (FO, LO, CW, Exhaust) systems | B |  |  | 2026-06-03 | Vendor reply: OK,please find the attachments | 已关闭 | 2026-05-19 | 2026-05-21 | 2026-06-18 | 2026-06-21 | √ | √ | √ | √ | 中标厂家。6.13提供了SCR资料，6.24提供了SCR电控接口图 | 2026-08-13
TA-0185 | DEMO-TA-M002-04 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家T | 船东 | 2026-06-03 | 提供控制箱布置草图 Provide Control Panel layout sketch | B |  |  | 2026-06-07 | Vendor reply: Will be supplied in approval drawing | 已关闭 | 2026-05-19 | 2026-05-21 | 2026-06-18 | 2026-06-21 | √ | √ | √ | √ | 中标厂家。6.13提供了SCR资料，6.24提供了SCR电控接口图 | 2026-08-13
TA-0186 | DEMO-TA-M002-04 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家T | 船东 | 2026-06-01 | 是否具备测试模式 Please let us know if there is a test mode | C |  |  | 2026-06-05 | Vendor reply: Don't have 【船东反馈】Kindly clarify how test run of the Em/cy generator is done | 已关闭 | 2026-05-19 | 2026-05-21 | 2026-06-18 | 2026-06-21 | √ | √ | √ | √ | 中标厂家。6.13提供了SCR资料，6.24提供了SCR电控接口图 | 2026-08-13
TA-0187 | DEMO-TA-M002-04 | 停泊/应急发电机组 Harbour/Emergency Generator | 厂家T | 船东 | 2026-06-03 | 提供售后服务网络 General. Please provide after-sales service network | C |  |  | 2026-06-06 | Vendor reply: You can find the local service in the below link: https://locator.cummins.com/GlobalLocator/homeScreen.action?request_locale=en_US# | 已关闭 | 2026-05-19 | 2026-05-21 | 2026-06-18 | 2026-06-21 | √ | √ | √ | √ | 中标厂家。6.13提供了SCR资料，6.24提供了SCR电控接口图 | 2026-08-13
TA-0188 | DEMO-TA-M001 | 柴油发电机组及 SCR 系统 Diesel Engines & SCR system | 厂家U | 船厂 | 2026-10-24 | 认可资料中总装图、电气接口资料尚缺，请厂家尽快提供，以满足详细设计及接口确认进度 | B |  |  |  |  | 待回复 | 2026-05-29 | 2026-06-03 | 2026-06-28 | 2026-07-02 | √ | 缺 | √ | 缺 | 提供了SCR以及消音器和MDL，6.30提供电气资料太晚了。 6.13提供内部PID及SCR模型文件，6.19提供了主机参数，6.20提供了更新的GA，设备清单，6.23提供了散热量计算书
TA-0189 |  |  |  | 船东 | 2026-11-05 | [6 empty] | 待回复
Note on P2: 「计划时间」即计划定标日，A类意见的要求回复时间受其约束
Note on H3: A：影响设备功能和大件订货 B：过程中可处理，不影响整体推进 C：认可后关闭
Note on J3: 【公式自动】提出时间 + 回复时限（参数表）；A类不晚于「定标计划·计划时间」（即计划定标日，且须在提出时间之后）
Note on W3: 认可函（图纸/设备资料认可函）的实际下发日期

## 参数表
参数表（下拉清单与时限，改这里即可）
意见类别 | 回复时限（天） | 判定标准
A | 3 | 影响设备功能、性能、选型、供货范围或价格，影响定标/大件订货（要求回复时间不晚于计划定标日）
B | 5 | 需修改资料/图纸，但可在过程中消化，不影响整体推进
C | 5 | 仅要求提供信息或确认，认可后关闭
临期阈值（天） | 3
下拉清单
意见提出方 | 意见类别 | 关闭状态 | 认可资料
船东 | A | 待回复 | √
船厂 | B | 已回复待确认 | NA
| C | 已认可待落实 | 缺
已关闭
说明：关闭状态中「已关闭」视为已结束，其余（待回复/已回复待确认/已认可待落实）为未关闭。